CUSTOMER SERVICE REPORT

| REPORT DATE | 26-08-2025 17:31 | REPORT NO | SRN-4743279 |
| --- | --- | --- | --- |
| COMPANY NAME | LVDSC INDUSTRIES PRIVATE LIMITED | CALL TRACKING NUMBER | CC-01778097 |
| SITE PERSON NAME | Mr Vinayak | TYPE OF CALL | Complaint - Running With Problem |
| SITE PERSON NUMBER | 7018643657 | FABRICATION NUMBER | 24018501 |
| SITE PERSON EMAIL ID |  | MODEL | ELRD-040 AIR DRIER |
| SITE LOCATION |  | PRODUCT | Recip - ACCESSORIES (RECIP) |
| SALE DEALER |  | PRE COMMISSIONING DATE |  |
| SERVICE DEALER | SERVICE EQUIPMENT COMPANY - CU1S02585 (Chandigarh) | COMMISSIONING DATE | 20-10-2024 |
| AMC STATUS | No AMC | WARRANTY STATUS | Out of Warranty |
| AMC REGISTRATION NO |  | LOAD HMR | 0 |
| AMC TYPE |  | UNLOAD HMR | 0 |
| AMC VISIT NO |  | TOTAL HMR | 0 |

| PARAMETERS | ACTUALS | RESPONSE |  | REPLACED DATE |
| --- | --- | --- | --- | --- |
| Suction temperature (°C) | 18 |  |  |  |
| Discharge temperature (°C) | 150 |  |  |  |
| Condenser outlet temperature (°C) |  |  |  |  |
| Inlet air temperature (°C) | 35 |  |  |  |
| Outlet air temperature (°C) | 24 |  |  |  |
| Room temperature (°C) | 38 |  |  |  |
| Ambient temperature (°C) | 36 |  |  |  |
| Dew point (°C) | 2 |  |  |  |
| Idle pressure (psi) | 100 |  |  |  |
| Suction pressure (psi) | 26 |  |  |  |
| Discharge pressure (psi) | 150 |  |  |  |
| Fan motor cut in/cut off settings (psi) | 180 |  |  |  |
| Incoming single phase voltage (volts) | 225 |  |  |  |
| RY - Incoming voltage (volts) | 234 |  |  |  |
| YB - Incoming voltage (volts) | 235 |  |  |  |
| BR - Incoming voltage (volts) |  |  |  |  |
| Earth to Neutral voltage (volts) |  |  |  |  |
| Incoming single phase current (amps) | 240 |  |  |  |
| R - Incoming current (amps) |  |  |  |  |
| B - Incoming current (amps) |  |  |  |  |
| Y - Incoming current (amps) |  |  |  |  |
| Fan Motor Current (amps) |  |  |  |  |
| Refrigerant compressor current (amps) |  |  |  |  |
| Refrigerant compressor resistance value (ω) |  |  |  |  |
| Is the ADV (ON/OFF) functioning |  | Yes |  |  |
| Is the Fan motor (ON/OFF) functioning |  | Yes |  |  |
| NO OF VISITS MADE |  |  |  |  |
| PARTS RECOMMENDED FOR SERVICE |  |  |  |  |
| WORKDONE | Change the air dryer main warning and air dryer working ok att the site. |  |  |  |
| PARTS DUE FOR NEXT SERVICE |  |  |  |  |
| Oil Remaining Hours | 0 |  |  |  |
| Oil Replaced Date |  |  |  |  |
| Type of Oil |  |  |  |  |
| NEXT SERVICE HMR |  | NEXT SERVICE DUE ON |  |  |
| IS THE SERVICE CHARGES APPLICABLE | No | SERVICE CHARGES | ₹ 0.00 |  |
| ENGINEER | Rajneesh Kumar | CONTACT NO | 6239504730 |  |
| DEALER | SERVICE EQUIPMENT COMPANY - CU1S02585 (Chandigarh) |  |  |  |
| CUSTOMER FEEDBACK | Satisfied - |  |  |  |
| ENGINEER REMARKS |  |  |  |  |

| NAME | SIGNATURE |
| --- | --- |